C O N T E N T S

page:

1.	description of assignment	7

2.	results of engineering geologic surve	7

3.	description of foundations of the construction uniT	8

3.1	foundations on the existing concrete slab	8

3.2	FOUNDATIONS 600 X 600	8

3.3	foundations for silos and common foundation for sorting drum and conveying belts	8

3.4	foundation slab close to the row 5	8

3.5	foundations for urea store	8

3.6	modification on the roof	8

4.	actions on structures	9

5.	USED MATERIALS	9

6.	Technological conditions of work progress and anti-corrosion protection	9

7.	List of standards and applied documents	9

8.	Requirements for safety during implementation	10

# description of assignment

The part of the project “Concrete Structures” resolves foundations of the technological units, located in the construction unit 103/1. Foundations from the conveyers, the integral part of PS 103/1, but located upstream the construction unit 103/1, are included in the construction unit 411.

# results of engineering geologic surve

The engineering geologic survey of the foundation soil was carried out for construction of the unit 401 -  “After-sorting and Turbine Hall” and processed by Geotest Brno, a.s. in February 2008. Geotest made two static penetration probes and two dynamic penetration probes. Further on, the archive probe V23 is recorded - from the survey carried out in 1979. The survey was not carried out in the hall 103, but the excavation plan for the original foundations is available, incl. description of subsurface conditions of the original  structural analysis:

«....on the perimeter of the site of the construction unit 103 there are the probes V28, V31, V34, V32.... gravels can be found at the depth of -5.6m; according to the probe V34 the gravels can be found at the depth from -5.8m. In the north-east direction the loess loams are thicker (probe V32 – gravel level -7.0m) », but the height level of the probe outlet is not known, we assume ca 249 m a.s.l.

The original excavation was designed at the level of 242,30m a.s.l., hall foundations are designed at the depth of ca 242.50 on the concrete subfloor layer 200 mm thick. Foundations for the technology were designed up to the depth of -1.80m under the floor ±0. The continuous excavation was made for the footing in the rows „H“ and „K“. The remaining soil inside the hall was removed up to the depth of -1.8m. Backfill is made of compacted gravel sand.

The original soil is created by the solid loess loam F6Cl. The gravel terrace can be awaited at the depth of ca 5.8m. The gravels are classified by the class G4 GM, settled. Penetration has revealed Id = 0.7 to 0.95; Eoed = 150MPa. According to the archive survey Edef = 90MPa, which corresponds to Eoed = 120MPa.

The underground water level can be found at the depth of ca 40 m.

The corrosive survey was processed by SIHAYA, spol.s r.o., in January 2008. The resultant degree of aggressivity is IV. Aggressive action of the environment on steel is very high. The basic protective measures from stray currents are preset in conformity with TP124 MDS, degree 4.

# description of foundations of the construction uniT

## foundations on the existing concrete slab

New foundation footing, protected from shift by the glued reinforcement, will be topped on the existing concrete slab. If the new foundation lies above the expansion (joint) of the existing slab, then connection of the new foundation and the old slab will be realized only on the greater area of both parts and the smaller area of the foundation will be separated from the original slab by a solid bituminous strip (bitagit S).

## FOUNDATIONS 600 X 600

The foundation is designed as the reinforced concrete block up to the depth of -0.200 under the floor. The floor will be cut away and cast in with the new foundation block. The joint between the old and new concrete will be sealed by the permanently elastic adhesive.

## foundations for silos and common foundation for sorting drum and conveying belts

The foundations continue the existing foundations for the original technology, having the footing bottom at the level of -1.8m. We assume that the old backfills are settled (were compacted adequately and/or their additional settling took place during operation). The foundations are designed as the reinforced concrete blocks with the footing bottom 1.0 m under the floor of the hall, turned monolithic with the original blocks by the glued reinforcement.

## foundation slab close to the row 5

The existing pit will be filled by compacted gravel sand. Compaction must be made to min. Id = 0,8, and/or Edef = 40 MPa. The reinforced concrete slab 200 mm thick will be laid on the backfill. The slab is not self-supporting. In order to observe the deformation criteria the slab is seated into the claw all its perimeter long.

## foundations for urea store

Foundation footing of plain concrete will be made for the main columns of the urea store. The footing close to the row „H6“ will be cast on the area of the existing hall footing. The footing close to the row „H5“ will be anchored to the existing structures by the glued reinforcement - to observe the deformation criteria. The central footing close to the row „5“ is seated on the compacted backfill - see section 3.4. Central footing close to the rows „6“ and „7“ is seated on the old concrete blocks left from the original technology.

## modification on the roof

Modifications on the roof include cutting of holes in the roof cladding and roof panels - for welding of the new steel columns to the existing steel beams. Prior to cutting the holes, the existing steel beams must be modified so that seating of the roof slabs (see part of the steel structure) may be provided. Hole in the roof slab will be cast after erection of the column. Casting will provide transfer of horizontal forces into the roof cladding.

It is also assumed that the stands for the new conveyers will be mounted on the roof. The max. additional loading of the roof panels by the conveyer column can be found in the chapter 4.

# actions on structures

As specified and preset, truck with the axle load of 13t will move on certain places of the floor. The original floor is designed for truck loading. The original floor is preserved in the hall, because it does not show any evident defects.

The foundations designed on the existing floor slab, load the slab up to 70 kPa.

The original backfills under the new foundations are loaded by max. 150 kPa.

New conveyer will be laid on the floor. Max. additional load of the roof panel by one load in the middle of the span is 4.1 kN. Panel width: 0.6m, panel length: 3m. Individual assessment is needed for higher load

# USED MATERIALS

The foundations are designed of the concrete C 25/30 XC2, coverage of underground structures is chosen min. 45mm. Concrete or non-conductive expansion blocks must be used for casting. In order to increase el. resistance, prior to backfilling the side areas of reinforced concretes will be provided by the bituminous coating ALP-M: 1x penetration + 1x top coating.

No protective measures and actions from stray currents are preset for foundations under the floor, because adequate separation of the floor from subbase by the original insulation is assumed.

# Technological conditions of work progress and anti-corrosion protection

Standard technological procedures will be observed during implementation. Piles will be erected from the original outdoor area into excavation.

Concrete reinforcement of underground structures will be welded together in the edges on the perimeter of the unit and/or at the 6 m spacing in cross sections.

The anti-corrosive protection comprises side coating of backfilled foundations.

# List of standards and applied documents

ČSN 73 0035-86	Actions on Structures

ČSN 73 0037-90	Earth Pressure Acting on Structures

ČSN 73 1001-87	Foundation Soil under Flat Foundations

ČSN 73 1201-86 	Concrete Structure Designing

ČSN EN 206-1 	Concrete – Part 1: Specifications Properties, Manufacture and Conformity

ČSN P ENV 13670-1 Concrete Structure Implementation – Part 1: Common Provisions

FINE, s.r.o., GEO 5 – Footings, Pilesl

NEXIS 32

CNIM documents

Engineering-geological survey Brno – Refuse Incinerating Plant. Turbine and After -sorting Hall. Geotest Brno, February 2008.

Corrosive survey. SIHAYA, spol.s r.o., January 2008

# Requirements for safety during implementation

Project documentation and structural analysis have been elaborated based on the design basis handed over by the customer. Calculations were carried out in conformity with valid Czech standards in the sector of structure designing and actions on structures.

When implementing, valid CSN standards for individual building works shall be observed. A great emphasis must be paid in particular to observance of technical, technological and quality procedures (steel structure welding, concrete mix processing, concrete treatment, duration of formwork removal, actions on reinforced concrete structures by concreting, extreme temperatures and excessive humidity, etc.) During all stages of implementation stability of the erected structures must be provided.

When implementing, building activities must be coordinated with projects of other professions (HVAC system, wiring, sanitary installations, central heating). If holes and grooves affect the supporting structures, consultations are needed regarding possible reinforcement or modification of the supporting elements and units.

During realization of the building works the Government Decree No. 362/2005 Sb. and the Government Decree No. 591/2006 Sb. concerning safety of labour and technical equipment during building works have to be observed and met as well as the Government Decree No. 361/2007 Sb., determining conditions of occupational health protection. The supplier is liable for observing the Decrees above.