C O N T E N T S

page:

1.	Description of assignment	6

2.	Results of engineering geologic survey	6

3.	Description of foundations of the construction unit	7

3.1	Foundations on the existing concrete slab	7

3.2	Foundation for silo	7

3.3	Foundations for fgd (flue-gas desulphurization) scrubber	7

4.	Actions on structures	7

5.	Used  materials	7

6.	Technological conditions of work progress and anti-corrosion protection	7

7.	List of standards and applied documents	8

8.	Requirements for safety during implementation	8

# Description of assignment

The part of the project “Concrete Structures” resolves foundations of the technological units, located between the construction unit 103/1 and the construction unit of the second flue gas cleaning stage. The project also includes foundation for PS 103/1, located in front of (upstream) the construction unit 103/1.

# Results of engineering geologic survey

The engineering geologic survey of the foundation soil was carried out for construction of the unit 401 -  “After-sorting and Turbine Hall” and processed by Geotest Brno, a.s. in February 2008. Geotest made two static penetration probes and two dynamic penetration probes. Further on, the archive probe V23 is recorded - from the survey carried out in 1979. The survey was not carried out in the hall 103, but the excavation plan for the original foundations is available. Neither the data concerning the engineering geologic survey nor the original project documents are available for the area of the construction unit 411 itself.

The original foundations are made to the depth of ca -5.6m from ±0 = 285.15. The newer concrete blocks were made on the concrete area.

Quantities of the made-up ground can change materially in individual parts of the area in question. We assume compacted gravel sand, module Edef ≥ 25MPa

The original soil is created by the solid loess loam F6Cl, Edef = 3MPa. The gravel terrace can be awaited at the depth of ca 5.5m. The gravels are classified by the class G4 GM, settled. Penetration has revealed Id = 0.7 to 0.95; Eoed = 150MPa. According to the archive survey Edef = 90MPa, which corresponds to Eoed = 120MPa.

The underground water level can be found at the depth of ca 40 m.

The corrosive survey was processed by SIHAYA, spol.s r.o., in January 2008. The resultant degree of aggressivity is IV. Aggressive action of the environment on steel is very high. The basic protective measures from stray currents are preset in conformity with TP124 MDS, degree 4.

# Description of foundations of the construction unit

## Foundations on the existing concrete slab

New foundation footing, protected from shift by the glued reinforcement, will be topped on the existing concrete slab. If the new foundation lies above the expansion (joint) of the existing slab, then connection of the new foundation and the old slab will be realized only on the greater area of both parts and the smaller area of the foundation will be separated from the original slab by a solid bituminous strip (bitagit S). The slab level ranges from 247.60 to 247.9 m a.s.l. The anchoring areas are at the level of 248.35 m a.s.l.

## Foundation for silo

The foundation is designed as a horizontally laid slab separated from the existing hall footing. In order to homogenize the footing bottom, it is proposed to dig up the footing bottom by 500 mm and to backfill it by compacted gravel sand. Compaction must be made to min. Id = 0.8. Footing bottom load is 120 kPa

## Foundations for fgd (flue-gas desulphurization) scrubber

Pile foundations are designed for scrubber columns. One pile under each column. For purpose of feasibility of the piles close to the transport bridge structure, two piles are designed with excentricity of 500 mm. Bending stress of the pile will be reduced by the continuous footing. Pile heads are designed above the piles.

# Actions on structures

Piles under the FGD scrubber foundation:

The maximum operating load of the pile from permanent and imposed load and from wind is assumed at the level of 1840 kN, in case of 9 mm settlement. Max. unloading (relief) at the stage of operation is -240 kN, at the stage of erection/assembly -380 kN.

Silo foundation:

Extreme load of the footing bottom is 134 kPa.

Foundations on the existing concrete slab:

Operating load at the slab level does not exceed 100 kPa for smaller foundations.

# Used  materials

The foundations are designed of the concrete C 25/30 XF3, coverage is chosen min. 45mm. Concrete or non-conductive expansion blocks must be used for casting. In order to increase el. resistance, prior to backfilling the side areas of reinforced concretes will be provided by the bituminous coating ALP-M: 1x penetration + 1x top coating.

# Technological conditions of work progress and anti-corrosion protection

Standard technological procedures will be observed during implementation. Piles will be erected from the original outdoor area into excavation.

Concrete reinforcement will be welded together on the perimeter of the unit and/or at the 6 m spacing in cross sections.

The anti-corrosive protection comprises side coating of backfilled foundations.

# List of standards and applied documents

ČSN 73 0035-86	Actions on Structures

ČSN 73 0037-90	Earth Pressure Acting on Structures

ČSN 73 1001-87	Foundation Soil under Flat Foundations

ČSN 73 1002-87	Pile Foundations

ČSN 73 1201-86 	Concrete Structure Designing

ČSN EN 206-1 	Concrete – Part 1: Specifications Properties, Manufacture and Conformity

ČSN P ENV 13670-1 Concrete Structure Implementation – Part 1: Common Provisions

FINE, s.r.o., GEO 5 – Footings, Piles

NEXIS 32

CNIM documents

Engineering-geological survey Brno – Refuse Incinerating Plant. Turbine and After -sorting Hall. Geotest Brno, February 2008.

Corrosive survey. SIHAYA, spol.s r.o., January 2008

# Requirements for safety during implementation

Project documentation and structural analysis have been elaborated based on the design basis handed over by the customer. Calculations were carried out in conformity with valid Czech standards in the sector of structure designing and actions on structures.

When implementing, valid CSN standards for individual building works shall be observed. A great emphasis must be paid in particular to observance of technical, technological and quality procedures (steel structure welding, concrete mix processing, concrete treatment, duration of formwork removal, actions on reinforced concrete structures by concreting, extreme temperatures and excessive humidity, etc.) During all stages of implementation stability of the erected structures must be provided.

When implementing, building activities must be coordinated with projects of other professions (HVAC system, wiring, sanitary installations, central heating). If holes and grooves affect the supporting structures, consultations are needed regarding possible reinforcement or modification of the supporting elements and units.

During realization of the building works the Government Decree No. 362/2005 Sb. and the Government Decree No. 591/2006 Sb. concerning safety of labour and technical equipment during building works have to be observed and met as well as the Government Decree No. 361/2007 Sb., determining conditions of occupational health protection. The supplier is liable for observing the Decrees above.