| F |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| E |  |  |  |  |  |  |  |  |  |
| D |  |  |  |  |  |  |  |  |  |
| C |  |  |  |  |  |  |  |  |  |
| B | 3105/2010 |  | Skutečný stav / As built |  |  |  |  |  |  |
| A | 20/02/2009 |  | Vydání první / First issue |  |  |  |  |  |  |
| Revize / Rev. | Datum / Date |  | Změny / Modifications |  |  | Kontrola/Checked |  | Schváleno / Approved |  |
|  |  |  |  | Uživatel / Employer |  |  |  |  |  |
|  |  |  |  | SAKO Brno, a.s. Jedovnická 2 628 00 BRNO Česká Republika |  |  |  |  |  |
| STAVBA / PROJEKT : PROJEKT ODPADOVÉ HOSPODÁŘSTVÍ BRNO CONSTRUCTION SITE / PROJECT : WASTE MANAGEMENT BRNO PROJECT |  |  |  |  |  |  |  |  |  |
| - PROJEKTOVÁ DOKUMENTACE : SKUTEČNÝ STAV DESIGN STAGE : AS BUILT |  |  |  |  |  |  |  |  |  |
| Provozní soubor / Operating unit - DPS 410.3 – Elektronické zabezpečovací zařízení DPS 410.3 – Electronic security equipment |  |  |  |  | Profesní část / Discipline - ELEKTRO - SLABOPROUD ELECTRO – WEEK CURRENT |  |  |  |  |
| Název dokumentu / Title of document Technická zpráva Technical report |  |  |  |  | Vydavatel / Issuer Evropská 33a 160 00 Praha 6 Česká republika |  |  |  |  |
| Inženýr / Engineer TENZA, a.s. Svatopetrská 7 617 00 BRNO Česká Republika |  |  |  |  |  |  |  |  |  |
| Konsorcium / Consortium CNIM 18, rue Grange Dame Rose 78457 VELIZY VILLACOUBLAY Cedex France Siemens s.r.o. Evropská 33a 160 00 PRAHA 6 Česká Republika |  |  |  |  | Vydavatel (subdodavatel) / Issuer (sub-supplier) Mariánské nám. 1 617 00, Brno Interní ref. č./Internal ref.: DDP 4103/GT E3201 B |  |  |  |  |
| Tento dokument je vlastnictvím společnosti Siemens. Nesmí být rozmnožován, šířen anebo zveřejňován bez předchozího písemného souhlasu Siemens. This document is property of Siemens. It cannot be used reproduced, transmitted and/or disclosed without the prior written permission of Siemens |  |  |  |  |  |  |  |  |  |
| Strana / Page 2 / 13 |  | Dokument č./N° document : 4048 1676/SI E3201 |  |  |  |  | Revize/ Rev./ : B |  | Status/ Statute/ : CAE |

REVIZE / REVISION

| Rev. Rev. | Datum/Předmět Date / Subject | Autor/Writer |  | Kontrola/Checked |  | Schválení/Approved |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Jméno/ Name | Podpis/ Visa | Jméno/ Name | Podpis/ Visa | Jméno/ Name | Podpis/ Visa |
| A | 20/02/2009 | R. Bosák |  | P. Kroutil |  | Krška |  |
|  | Vydání první / First issue |  |  |  |  |  |  |
| B | 31/05/2010 | R. Bosák |  | P. Kroutil |  | Krška |  |
|  | Skutečný stav / As built |  |  |  |  |  |  |
| C |  |  |  |  |  |  |  |
| D |  |  |  |  |  |  |  |
| E |  |  |  |  |  |  |  |
| F |  |  |  |  |  |  |  |
| G |  |  |  |  |  |  |  |
| H |  |  |  |  |  |  |  |
| J |  |  |  |  |  |  |  |
| K |  |  |  |  |  |  |  |
| L |  |  |  |  |  |  |  |
| M |  |  |  |  |  |  |  |
| N |  |  |  |  |  |  |  |

S U M M A R Y

1.	TECHNICAL REPORT                                                                                                                       4

1.1	INTRODUCTION	4

1.2	BASIC DATA FOR THE PREPARATION OF THE DOCUMENTATION	4

1.3	USED STANDARDS	4

2.	TECHNICAL SOLUTION OF THE DESIGN                                                                                       5

2.1	INTRODUCTION	5

2.2	DESCRIPTION OF THE SOLUTION	5

2.2.1	TECHNICAL CHARACTERISTICS OF THE USED EQUIPMENT                                          6

2.3	SUPPLY NETWORK	10

2.4	CABLE WAYS AND CABLES	10

2.5	AMBIENT ACC. TO ČSN 33 2000-5-51	11

2.6	ELECTRIC SHOCK PROTECTION ACC. TO ČSN 33 2000-4-41	11

2.7	FIRE PRECAUTIONS	11

2.8	MEASUREMENT CHECK	11

2.9	ELECTRIC ENERGY REQUIREMENTS	12

2.10	WASTE DISPOSAL	12

# TECHNICAL REPORT

## INTRODUCTION

Electronic security signalling /ESS/ and access control system /ACS/ are the matters of this detail design documentation. This documentation does not solve ESS and ACS in the administration building. The documentation includes the electronic security equipment diagram and ground plans of appropriate floors.

## BASIC DATA FOR THE PREPARATION OF THE DOCUMENTATION

The design documentation was based on:

- Ground plans of individual floors

- Investor’s requirements for technical characteristics of the designed systems

- As-built documentation – ESS, ACS, CCTV

- Consultation with the user’s representative

- Consultation with the design chief engineer and with compilers of consequential professions

## USED STANDARDS

At the realization of weak current equipment following ČSN standards have to be respected (have been used for the preparation of the design documentation):

ČSN 33 2000-3	Electrical regulations for the electric equipment – determination of basic characteristics

ČSN 33 2000-4-41 ed.2	LV electric installations - Part 4-41: Safety protection measures – Electric shock protection

ČSN 33 2000-5-51 ed.2	Electric installations in buildings – Part 5-51: Selection and construction of electric equipment - general regulations

ČSN 33 2000-5-52 ed.2	Electrical regulations for the electric equipment – Part 5-52: Selection of systems and installation of power lines

ČSN 33 2000-5-54 ed.2	LV electric installations – Part 5-54: Selection and construction of electric equipment - Earthing, safety conductors and safety interconnection conductors

ČSN 33 2000-6	LV electric installations – Part 6: Revisions

ČSN EN 50 131-1		Alarm systems – Electric safety systems

# TECHNICAL SOLUTION OF THE DESIGN

## INTRODUCTION

ESS system provides an on-time signalling at a violation. No necessary mechanical barriers in the watched area are substituted.

According to ČSN EN 50131-1 the object has been categorized as level 2: Low and middle risks.

This design solves:

- A change of the control SW of the upgrade of the existing access system for an integration with the ESS system – all existing relations to other systems will be kept.

- A delivery of new working stations for the SW upgrade.

- A completion of the existing access control system with a door spring to the new-built control room of the incinerator.

The design expected:

- An interconnection of both working stations with LAN-network (other access and attendance system components have been already connected with this network). This interconnection is realized within the design of LAN extension.

## DESCRIPTION OF THE SOLUTION

The existing access system is based on the components of the integrated system of the Apollo-company. With these components – after the completion of the SW upgrade APACS – it is possible to build an integrated system that complexly solve ESS, access and attendance integration, possibly also the integration of CCTV.

The system is designed so that to minimize demands for an active system service in idle mode. Most functions of the system will be automatic. In case of alarm conditions the alarm will be signalled both – sound and optic, with graphic and text.

The designed SW Apollo APACS is able to integrate ESS, ACS and CCTV systems, to visualize CS information (installed in the object Jedovnická and the object of the collection), to configure the system, to administer identification cards and to do other services.

The program Apollo APACS server is able to communicate – through the LAN network - with possible new control units. The existing control units communicate with individual concentrators, modules of card sensor connections and with the existing working stations through the interface RS-485, possibly RS-232.

The new designed software system upgrade (visualization and control), including two working stations and monitors, are installed on two sites – in the control room and in the main gatehouse. The system expects a permanent presence of the security staff or of the control room operator.

The system configuration is recorded in the control unit memory, i.e. the operation can be fully autonomous, even at the upgrade program failure. In addition, the autonomous concentrators and the modules of the card sensor connections have their own memories that enable busbar-functionality at a failure of the communication with the control unit.

A door spring (is installed within this design documentation) is communication-interconnected with the existing control unit that is installed in the gatehouse and is included to this control unit‘s configuration, as well as the new-installed concentrator of the alarm loops AIO 168.

Within the framework of this project following equipment are installed on the door spring in the entrance to the control room in SO 401:

- identification cards sensor, compatible with the existing identification cards technology - 2 pc,

- magnetic contact – 2 pc

- electric-mechanic lock with a fitting and a cable adapter Abloy (a concrete type installation accessories must be a part of the door delivery).

- “electric porter” included to the external intercom speech sound system that is solved in DPS 410.1 – Telephone equipment – 1 pc

(to open the electric-magnetic lock: will be possible also by a password that will be entered by a tone dialling from appropriate phone sets in the control room).

For the layout of the integrated system parts in the social and administration building see dwg. No. DDP4103_GTG1206B.

Identification card sensors are installed on both – incoming and outgoing sides. Sensors and magnetic contacts are connected to the AIM-1SL sensor module that is installed in the SE electronics box together with the ESS loop concentrator, AIO168 type. This box includes also a standby supply 13,8 Vss and a standby battery. The box is supplied from the field 9b, outlet 822 of the power switchboard RM405. The box is communication-connected (by a communication line RS485) with the existing access system in the place of the installation of the box of the door spring electronics (the door springs is installed in entries to the existing control room in v SO 106).

Another ESS system and technology sensors (especially if there is a logic relationship to the safety system, e.g. escape sensors of various gases or active principles, flood sensors, radioactivity detection, etc.) can be additionally connected to the system by the concentrators of AIO168 loops, if necessary.

A connection between an initiatory event (any sensor detection) and a related reaction (closing of the power element) can be done in the system automatically. Because of a high reliability, this is done on the control unit level (not in PC program).

### TECHNICAL CHARACTERISTICS OF THE USED EQUIPMENT

Existing control unit AAN - 100

The control unit AAN-100 is the basis of the existing Apollo integrated system. 4 busbars with RS 485 (slave) interfaces and 2 communication lines, e.g. for PC, LAN or a printer (guest) with RS 232/485/ Ethernet 100Base-T interface can be connected by as much as 6 plug-in communication modules of various designs. The PC communication module in LAN is marked ANI-100.

Basic specification

Dimensions (LxWxH):				19 x 14 x 2,5 cm

Operational temperature limit:			 0 to 500C

Operational environment:			humidity 0-95 %, non-condensable

Current consumption (13,6-28 VDC):		400 mA with 1 pc ANI-1OO

Spare battery:					3 pc alkaline battery, size AA

Basic characteristics

Firmware is stored in a memory of flash 2 Mb type

Plug-in communication and memory modules

Direct support of the connection to LAN (100 Mbit) by the ANI-100 module

TCP/IP protocol (with the module ANI 100 and ENI 100, ENI 110)

Support at a connection of the RS 232/485 interface with optic cables

6 communication ports

Standard-delivered memory 1MB RAM, extensible up to 8 MB

Memory for up to 250000 card owners/100000 events

Battery-backed up supply of database and event memory

Support of up to 32 input-output modules (1280 zones)

Direct control of 64 card sensors

Lift control/anti-passback/alarm screen

Application

AAN-100 control unit can communicate with contact-less card sensors with the wiegand interface by the modules of the connection of AIM-1SL, possibly 4(SL) sensors. A standard delivery is with 1 MB RAM memory that is extensible by plug-in modules AME-10 or AME-20 up to 8 MB. For the communication with the technology equipment up to 4 communication units of various types (ASM-23, ASM-48 or ENI 100/110) can be installed. The communication module ANI-100 is for the connection to the local LAN network. This module is equipped with the connector RJ-45/AUI.

Cabling

Ethernet				2 unscreened TP

Category 3, 4, or 5

100 m max.

RS  485				2 x TP screened, impedance 120 Ohm,

Belden 9842, SYKFY 3x2x0,5

1200 m max.

RS 232				5 conductors, screening (SYKFY 3x2x0,5)

15 m max.

Connection module of AIM – 1SL card sensor

AIM-1SL card sensor connection module is an interface for identification card sensors with a local database. There are: outlets for 2 sensors with Wiegand interfaces, 3 colour LED diodes and a buzzer. Can be used with 2 sensors (a possibility of anti-passback-mode) or with one sensor and with an outlet push-button. Each sensor can be equipped with a keyboard for PIN-entry. In the unit there is built 2A relay for the electric lock control. Can be also connected to an external relay module ADA 10/11 or ADA 20/21.

The unit has an inlet for a door magnetic contact and two auxiliary inlets. AIM-1SL unit cooperates with AAN control units in the integrated access and safety system Apollo.

dimensions: 		189,87 x 101,60 mm

local database size: 	20 000 cards, 7000 events

1-2 sensors with/without a keyboard

4 balanced inlets

1 internal relay (possible connection of 4 external relays)

Inlet for a protective box contact

actual time

Application

The connecting module AIM-1SL is for a complete connection of 1 door spring, especially to the integrated access and safety system Apollo. The door spring can be made of two inlet identification card sensors, possibly with a keyboard (with Wiegand interface), of an outlet (outlet push-button) magnetic door contact and an auxiliary contact inlet. The spring outlet is equipped with a contact relay for the lock. The connection module is also equipped with a digital outlet for a connection of up to 16 ADA modules.

The analogue inlets will recognize, if they are set for the „supervised inlets“ mode. Following conditions:

Idle condition

Alarm condition

failure

disconnected loop,

short-circuited loop

additional earthing

failure in hw circuits.

Cabling

RS  485				2 x TP screened, impedance 120 Ohm,

Belden 9842, SYKFY 3x2x0,5

1200 m

Leaving push-button		TP, max. length 150 m, 0,5 mm

Door contact			TP, max. length 150 m, 0,5 mm

Auxiliary inlet	                       TP, max. length 150 m, 0,5 mm

ESS AIO–168 loop concentrator

ESS AIO–168 loop concentrator is the basic loop module for the safety systems. 16 analogue inlets and 8 relay outlets are included.

Basic specification

Dimensions (LxWxH):				19 x 14 x 2,5 cm

Operational temperature limit:			0 to 700C

Operational environment:			humidity 0-95 %, non-condensable

Current consumption (12 - 28 Vss):		250 mA

Maximum analogue loop resistance:		30 Ω (measured without EOL)

Loop termination (EOL Terminator)		ATM-30 470-031, max. 30 cm from the sensor

Approx. distance from the sensor:		approx 450 m for the conductor 0,8 mm,

resistance check

Basic characteristics

Optional communication speed (300, 1200, 2400, 9600 Bd)

Plug-in communication module (LAN, RS485, RS 232)

1 communication port

16 analogue alarm inlets (UL Grade A)

8 contact outlets (C-NO-NC, 30 V, 1A)

Flash-memory for firmware

Address selection by DIP (32) switches

Memory of FIFO-type for an event backup at a communication failure (up to 100 alarms)

Tamper-contact of the box

Inlet for signalling of the supply-failure

2 diagnostic LEDs

Application

AIO-168 loop insertion includes 16 analogue inlets. Balanced analogue inputs („supervised inputs“) will identify following loop conditions:

- Idle condition

- Alarm condition

- failure

- disconnected loop,

- short-circuited loop

- additional earthing

- failure in hw circuits

that are signalled to the superior system. The conditions of alarm inputs are checked 240-times/sec. The recorded data are false-alarm-filtered.

At the same time AIO-168 monitors the tamper-contact of the box and a supply failure (NC-type contacts).

Cabling

RS 485			2 x TP screened, impedance 120 Ohm,

Belden 9842, SYKFY 3x2x0,5

1200 m max.

RS 232			5 conductors, screened (SYKFY 3x2x0,5), 15 m max.

Safety loops aprox. 450 m for the conductor 0,8 mm with a loop resistance check.

PC working station:

Minimum configuration:

Processor Intel Core 2 Duo E8400 or higher

2GB RAM, 160 GB HDD, CD/DVD ROM,

monitor 20"  TFT,

keyboard, mouse

OS Windows Vista Downgrade to XP Pro,

Connection to LAN network

Identification card sensors:

Compatible with the existing card sensor technology HID

## SUPPLY NETWORK

ESS centrals: 		1NPE AC 50Hz, 230V-TN-C-S

ESS concentrators: 	12V DC, SELV

The system elements are supplied by LV supply with their own standby batteries.

## CABLE WAYS AND CABLES

The cables are led in individual cable ways or in joint LV distributions. The cables are of metallic design.

## AMBIENT ACC. TO ČSN 33 2000-5-51

External effects (ambient type) for individual internal and external areas have been determined in the “Protocol on external effects” prepared by an expert committee of TKB Kovoprojekta Brno according to ČSN 33 2000-3 and ČSN 33 2000-5-51. This Protocol is a part of the “Accompanying Report” of the building permit documentation.

## ELECTRIC SHOCK PROTECTION ACC. TO ČSN 33 2000-4-41

Central – automatic disconnection from the supply

Detectors and distributions – by a safe voltage (operating voltage of the system is 12V DC).

## FIRE PRECAUTIONS

All ceiling and walls breakthroughs, as well as fire cell limits, are prepared as fire stops. On inlets and outlets through the walls and ceilings the cables are treated with a uniform fire system – is specified in the building part.

Each fire breakthrough must be equipped with a label with the company data and with the date of the installation.

## MEASUREMENT CHECK

The whole system was visually checked after the installation of all components, cables, units, readers, sensors and actuators is finished. A correct wiring, a full and correct marking were checked too.

All installed cabling outlets were measured. Consequently all necessary functional tests of the system were done and the system was commissioned.

Recognized values were stated in the revision report, possibly in an operational system record too.

The assembly and Service Company will provide regular revisions according to valid ČSN.

## ELECTRIC ENERGY REQUIREMENTS

ESS supply is supplied by an independently protected power outlet 230V/6A AC from the field 9b, outlet 822 of the power switchboard RM405.

According to ČSN requirements, there is installed an overvoltage protection – class 3 in front of the inlet of power supplies to ESS. This protection is installed in a distribution box or in a type sleeve housing.

## WASTE DISPOSAL

To meet his/her supply contract provisions the supplier of  the electric assembly work must provide the waste disposal acc. to the Law No.106/2005 of Code on the wastes and according to the executive edicts No. 381, 383, 376/2001 and 115/2002.